## Lines
|  | CYME |  |  | DITTO
File | Header | Attribute | Units | Description | Attribute | Duplication Warning | Units | Description | Default
Equipment | [LINE] | ID | String | ID label of the line | name | None |  | The name of the line object
[LINE UNBALANCED]
[5 empty] | nominal_voltage |  | Volts | This parameter defines the base voltage of the wire. | None
Network | Get this information from the header: Overhead/Underground line |  |  |  | line_type | None | String | Whether the line is overhead or underground | overhead
Network | [OVERHEADLINE SETTING] | Length | km or miles | Length of the line. | length | None | Meters | This parameter is the length of the Line | None
[OVERHEADLINEUNBALANCED SETTING]
[UNDERGROUNDLINE SETTING]
Network | [SECTION] | FromNodeID | String | ID of the node | from_element | None | String | Name of the node which connects to the 'from' end of the line | None
Network | [SECTION] | ToNodeID | String | ID of the node | to_element | None | String | Name of the node which connects to the 'to' end of the line | None
Equipment | [FUSE] | Always True… |  |  | is_fuse | Needs to be consistant with wire values. True if one or more of the wires is a fuse | Bool | This flag indicates whether or not the line is also a fuse | None
Equipment | [SWITCH] | Always True… |  |  | is_switch | Needs to be consistant with wire values. True if one or more of wires is a switch | Bool | This flag indicates whether or not the line is also a switch | None
[5 empty] | is_banked | Needs to be consistent with all the switch positions of each phase. | Bool | This flag indicates whether or not the switch is banked. If this is true, the switch objects are controlled together | None
[5 empty] | faultrate | None | Float | The number of faults that occur per year | None
[5 empty] | wires | None | List(Wire) | This parameter is a list of all the wires included on the line. The wires are objects containing elements of phase, X and Y. | None
Network | [FUSE SETTING] | CoordX, CoordY | Float | X and Y coordinates of the fuse. | positions | None | List(Position) | This parameter is a list of positional points describing the line. The positions are objects containing elements of long, lat and elevation. The points can be used to map the position of the line. | None
| [OVERHEADLINE SETTING] |  |  | X and Y coordinates of the line.
[OVERHEADLINEUNBALANCED SETTING]
[UNDERGROUNDLINE SETTING]
[5 empty] | impedance_matrix | Needs to be consistent with wire values. It is either provided or derived from the wires. | List(List(Complex)) Ohms/meter | This provides the matrix representation of the line impedance in complex form. Computed from the values of GMR and distances of individual wires. Kron reduction is applied to make this a 3x3 matrix.
[5 empty] | capacitance_matrix | Needs to be consistent with wire values | List(List(Complex)) MicroSiemens/meter | This provides the matrix representation of the line capacitance in complex form. Computed from the values of diameter and distances of individual wires. Kron reduction is applied to make this t a 3x3 matrix.

## wires
|  | CYME |  |  | DITTO
File | Header | Attribute | Units | Description | Attribute | Duplication Warning | Units | Description | Default
Equipment | [SECTION] | Phase | phase | Phase on the section. | phase | None | String | The phase (A, B, C, N, s1, s2) of the wire
[5 empty] | nameclass | None | String | The nameclass (e.g. 1/0_ACSR) of the wire
Equipment | [SPACING TABLE FOR LINE] | PosOfCondx_X | float | Replace x by 1,2,3. For neutral: PosOfNeutralCond_X | X | None | Meters | The horizontal placement of the wire on a cross section of the line w.r.t. some point of reference (typically one wire on the configuration)
Equipment | [SPACING TABLE FOR LINE] | PosOfCondx_Y | float | Replace x by 1,2,3. For neutral: PosOfNeutralCond_Y | Y | None | Meters | The vertical placement above (or below) ground of the wire on a cross section of the line w.r.t. some point of reference (typically one wire on the configuration)
Equipment | [CABLE CONDUCTOR] | Diameter | ? | Diameter | diameter | None | Meters | The diameter of the conductor
[CONDUCTOR]
Equipment | [CONDUCTOR] | GMR | cm or inch | GMR | gmr | None | meters | The geometric mean radius of the wire
Equipment | [CABLE] | Amps | Amps | Ampacity | ampacity | None | Amps | The ampacity rating of the wire under normal conditions
[CONDUCTOR]
[FUSE]
[SWITCH]
Equipment | [CABLE] | WithstandRating | Amps | Not sure about this one… | ampacity_emergency | None | Amps | The ampacity rating of the wire under emergency conditions
[CONDUCTOR]
[5 empty] | resistance | None | Ohms | The total resistance of the wire
Equipment | [FUSE] | Always True… |  |  | is_fuse | None | Boolean | This flag indicates whether or not this wire is also a fuse
Equipment | [SWITCH] | Always True… |  |  | is_switch | None | Boolean | This flag indicates whether or not this wire is also a switch
Equipment | [SWITCH] | SymbolOpenID | Integer | Looks pretty close, but I don't understand how it works… | is_open | None | Boolean | This flag indicates whether or not this wire is open (if it is a switch/fuse)
Equipment | [FUSE] | InterruptingRating | Amps | Pretty confident but not 100% sure… | fuse_limit | None | Amps | This is the limit of the wire before the fuse blows
[5 empty] | concentric_neutral_gmr | None | Meters | The geometric mean radius of the neutral for a concentric wire
[5 empty] | concentric_neutral_resistance | None | Ohms | The total resistance of the neutral for a concentric wire.
[5 empty] | concentric_neutral_diameter | None | Ohms | The diameter of the neutral for a concentric wire.

## Node
|  | CYME |  |  | DITTO
File | Header | Attribute | Units | Description | Attribute | Duplication Warning | Units | Description | Default
Network | [NODE] | NodeID | String | ID label of the node | name | None |  | The name of the node object
[HEADNODES]
Network | [NODE] | RatedVoltage | Float | Rated voltage of the node | nominal_voltage | None | Volts | The nomial voltage of this node
Network | [SECTION] | Phase | phase | Phase on the section. | phases | None | List(String) | A list of the different phases at this node
Network | [NODE] | CoordX,CoordY | Float | X and Y coordinates of the node | positions | None | List(Position) | This parameter is a list of positional points describing the node - it should only contain one. The positions are objects containing elements of long, lat and elevation. | None

## Load
|  | CYME |  |  | DITTO
File | Header | Attribute | Units | Description | Attribute | Duplication Warning | Units | Description | Default
Load | [LOADS] | SectionID | String | ID for the customer class | name | None |  | The name of the load object
[CUSTOMER LOADS]
Network | [NODE] | RatedVoltage | Float | Rated voltage of the node | nominal_voltage | None | Volts | The nomial voltage of this node
Load | [LOADS] | ConnectionConfiguration |  | Connection configuration of the load | connection_type | None | String | The connection type (D, Y, Z, A) for Delta, Wye, Zigzag or autotransformer
[5 empty] | vmin | None | Float | The minimum per-unit voltage value. Going below this implies constant impedance
[5 empty] | vmax | None | Float | The maximum per-unit voltage value. Going below this implies constant impedance
[5 empty] | phase_loads | This has been adjusted from the original model so that all the load information is contained with different phases. | List(PhaseLoad) | This is a list of the different phase loads connected to the one load point. This contains information about the phase as well as the p&q or zip load data
Network | [SECTION] | FromNodeID | String | Get the SectionID to get the Node ID | connecting_element | None | String | Name of the bus the load is connected to | None
Network | [SECTION] | Get the position of the section or of the nodes |  |  | positions | None | List(Position) | This parameter is a list of positional points describing the load- it should only contain one. The positions are objects containing elements of long, lat and elevation. | None
[5 empty] | rooftop_area |  | Float | This parameter is the rooftop area for all phases of the load | None
[5 empty] | peak_p |  | Float | This parameter is the annual peak p value of all combined phases of the load | None
[5 empty] | peak_q |  | Float | This parameter is the annual peak q value of all combined phases of the load | None
[5 empty] | peak_coincident_p |  | Float | This parameter is the annual coincident peak p value of all combined phases of the load | None
[5 empty] | peak_coincident_q |  | Float | This parameter is the annual coincident peak q value of all combined phases of the load | None
[5 empty] | yearly_energy |  | Float | This is the total energy used by the load across all phases over a typical year | None
[5 empty] | num_levels |  | Float | The number of floors (levels) that the building load has | None

## PhaseLoad
|  | CYME |  |  | DITTO
File | Header | Attribute | Units | Description | Attribute | Duplication Warning | Units | Description | Default
Load | [CUSTOMER LOADS] | LoadPhase | phase | phase | phase | None | String | The phase (A, B, C, N, s1, s2) of the load
Load | [CUSTOMER LOADS] | Value1 | kW | Use ValueType to see what is provided. Could be P, Q, PF, or I | p | This is done specifically for this phase and is used when use_zip is 0 | Watts | The active power of the load which is fixed. Positive values represent flow out of the node.
Load | [CUSTOMER LOADS] | Value2 | kVAR |  | q | This is done specifically for this phase and is used when use_zip is 0 | Var | The reactive power of the load which is fixed. Positive values represent flow out of the node.
[5 empty] | use_zip | None | Int | Describes whether the load is reprsented as a zipload or not. 1 represents zipload with fractions taken from the p and q values above. 0 represents a load defined by p & q alone.
Load | [CUSTOMER CLASS] | ConstantCurrentIP | float | In between 0 and 100. OpenDSS between 0 and 1 | ppercentcurrent | This is the portion of active power load modelled by constant current. Active portions of current, power and impedance should all add to 1. Used for ZIP models.
Load | [CUSTOMER CLASS] | ConstantCurrentIQ | float | In between 0 and 100. OpenDSS between 0 and 1 | qpercentcurrent | This is the portion of reactive power load modelled by constant current. Reactive portions of current, power and impedance should all add to 1. Used for ZIP models.
Load | [CUSTOMER CLASS] | ConstantPowerPP | float | In between 0 and 100. OpenDSS between 0 and 1 | ppercentpower | This is the portion of active power load modelled by constant power. Active portions of current, power and impedance should all add to 1. Used for ZIP models.
Load | [CUSTOMER CLASS] | ConstantPowerPQ | float | In between 0 and 100. OpenDSS between 0 and 1 | qpercentpower | This is the portion of reactive power load modelled by constant power. Reactive portions of current, power and impedance should all add to 1. Used for ZIP models.
Load | [CUSTOMER CLASS] | ConstantImpedanceZP | float | In between 0 and 100. OpenDSS between 0 and 1 | ppercentimpedance | This is the portion of active power load modelled by constant impedance. Active portions of current, power and impedance should all add to 1. Used for ZIP models.
Load | [CUSTOMER CLASS] | ConstantImpedanceZQ | float | In between 0 and 100. OpenDSS between 0 and 1 | qpercentimpedance | This is the portion of reactive power load modelled by constant impedance. Reactive portions of current, power and impedance should all add to 1. Used for ZIP models.
[5 empty] | model |  | Int | OpenDSS load model number (1=constant P&Q, 8=ZIP,…)

## Capacitor
|  | CYME |  |  | DITTO
File | Header | Attribute | Units | Description | Attribute | Duplication Warning | Units | Description | Default
Equipment | [SERIE CAPACITOR] | ID | String | ID label of the capacitor | name | None |  | The name of the capacitor object
[SHUNT CAPACITOR]
Equipment | [SHUNT CAPACITOR] | KV | kV | Rated KV (line-to-neutral for wye-grounded, line-to-line for delta) | nominal_voltage | None | Volts | The nomial voltage of the capacitor
Network | [SHUNT CAPACITOR SETTINGS]
Network | [SHUNT CAPACITOR SETTINGS] | Connection | CAP_CONN | Connection type | connection_type | None | String | This is the type of connection that the capacitor has. The connection type (D, Y, Z, A) for Delta, Wye, Zigzag or autotransformer
[5 empty] | delay | None | seconds | The time that the capacitor needs to connect or disconnect by automatic regulation
Network | [SHUNT CAPACITOR SETTINGS] | Control | CAP_CONTROL | Control type | mode | None | String | What control mode is used. A string from one of the options: {voltage, activePower, reactivePower, currentFlow, admittance, timeScheduled, none}
[5 empty] | low | None | Volts, Var, Watt | The low value of range of the type being controllee by the capacitor (e.g. voltage)
[5 empty] | high | None | Volts, Var, Watt | The high value of range of the type being controllee by the capacitor (e.g. voltage)
[5 empty] | resistance | None | Ohms | The total series resistance of the capacitor
[5 empty] | resistance0 | None | Ohms | The total zero-sequence series resistance of the capacitor
Equipment | [SERIE CAPACITOR] | Reactance | Ohm | Reactance of the capacitor | reactance | None | Ohms | The total series reactance of the capacitor
[5 empty] | reactance0 | None | Ohms | The total zero-sequence series reactance of the capacitor
[5 empty] | susceptance | This should match the formula of -1*VAR/(voltage)^2 where var is the total Var of the capacitor and voltage is the nominal voltage | Siemens | The total positive sequence shunt susceptance of the capacitor.
[5 empty] | susceptance0 | None | Siemens | The total zero sequence shunt susceptance of the capacitor.
[5 empty] | conductance | None | Siemens | The total shunt conductance of the capacitor
[5 empty] | conductance0 | None | Siemens | The total zero sequence shunt conductance of the capacitor
[5 empty] | pt_ratio | None | Float | The voltage (potential) transformer ratio used to step down the voltage for the controller
[5 empty] | ct_ratio | None | Float | The current transformer ratio used to define the current ratio for a controller.
Network | [SHUNT CAPACITOR SETTINGS] | ControllingPhase | Phase |  | pt_phase | None | String | The phase that the controller is connected to
[5 empty] | connecting_element | None | String | The name of the node that the capacitor connects to
[5 empty] | measuring_element | None | String | The name of the element that the capControl is sensing (typically a line or a transformer). This is a required field for OpenDSS | None
Network | [SERIES CAPACITOR SETTINGS] | CoordX, CoordY | Float | X and Y coordinates of the capacitor | positions | None | List(Position) | This parameter is a list of positional points describing the capacitor - it should only contain one. The positions are objects containing elements of long, lat and elevation. | None
[5 empty] | phase_capacitors | None | List(PhaseCapacitor) | A list of phase capacitors which contain phase, var and switch values. The total var of the capacitor is defined through the phasecapacitors

## PhaseCapacitor
|  | CYME |  |  | DITTO
File | Header | Attribute | Units | Description | Attribute | Duplication Warning | Units | Description | Default
Network | [SHUNT CAPACITOR SETTINGS] | ControllingPhase | Phase |  | phase | None | String | The phase (A, B, C, N, s1, s2) of the capacitor section
Network | [SHUNT CAPACITOR SETTINGS] | FixedKVARA, FixedKVARB… | kvar | Fixed KVAR per phase | var | None | var | The var value of the capacitor phase
[5 empty] | switch | None | Int | A boolean value to denote whether or not the capacitor is switched in. 1 means it's switched in, 0 means that it's not.
[5 empty] | sections | None | Int | The maximum number of sections that can be connected to this phase
[5 empty] | normalsections | None | Int | The normal number of sections that are connected to this phase.

## Transformer
| CYME |  |  |  | DITTO
File | Header | Attribute | Units | Description | Attribute | Duplication Warning | Units | Description | Default
Equipment | [AUTOTRANSFORMER] | ID | String | ID label of the transformer | name | None |  | The name of the transformer object
[GROUNDING TRANSFORMER]
[THREE WINDING AUTO TRANSFORMER]
[THREE WINDING TRANSFORMER]
[TRANSFORMER]
[PHASE SHIFTER TRANSFORMER]
[5 empty] | install_type | None | String | The mounting of the transformer: one of {POLEMOUNT, PADMOUNT, VAULT}
Equipment | [AUTOTRANSFORMER] | NoLoadLosses | kVa | Total Transformer cooled rating according to Type value | noload_loss | None | per unit Ohm | The no-load loss for a zero sequence short circuit test across the entire transformer.
[THREE WINDING AUTO TRANSFORMER]
[THREE WINDING TRANSFORMER]
[TRANSFORMER]
Equipment | [TRANSFORMER] | PhaseShift | degree | Phase shift | phase_shift | None | Degrees | The degree phase shift that the transformer causes
Network | [AUTO TRANSFORMER SETTING] | FromNodeID | String | Parent section ID in the normal configuration | from_element | None | String | Name of the node which connects to the 'from' end of the transformer
[5 empty] | to_element | None | String | Name of the node which connects to the 'to' end of the transformer
[5 empty] | reactances | None | List((Int,Int,Int)) | Reactances are described between all the windings. There are n*(n-1)/2 reactances (where n is the number of windings). For two a winding transformer this gives one value, and for a 3 winding transformer it gives 3. The list elements have (from_winding, to_winding, reactance) where from_winding and to_winding are the 1-based indices of the windings list.
[5 empty] | windings | None | List(Winding) | A list of the windings that the transformer contains. Most will have two windings but center tap transformers have three.
[5 empty] | loadloss | None | Float | Percent Losses at rated load
[5 empty] | normhkva | None | Float | Normal maximum kVA rating for H winding
Network | [AUTO TRANSFORMER SETTING] | CoordX, CoordY | Float | X and Y coordinates of the transformer | positions | None | List(Position) | This parameter is a list of positional points describing the transformer - it should only contain one. The positions are objects containing elements of long, lat and elevation.
[THREE WINDING AUTO TRANSFORMER SETTING]
[THREE WINDING TRANSFORMER SETTING]
[PHASE SHIFTER TRANSFORMER SETTING]

## Winding
|  | CYME |  |  | DITTO
File | Header | Attribute | Units | Description | Attribute | Duplication Warning | Units | Description | Default
Equipment | [AUTOTRANSFORMER] | ConnectionConfiguration |  | Type of connection | connection_type |  | String | The connection type (D, Y, Z, A) for Delta, Wye, Zigzag or autotransformer
Network | [AUTO TRANSFORMER SETTING]
Equipment | [GROUNDED TRANSFORMER]
Network | [GROUNDINGTRANSFORMER SETTINGS]
Equipment | [TRANSFORMER] | Conn
[5 empty] | voltage_type |  | Int | 0 for a high voltage connection, 2 for a low voltage connection and 1 for an intermediate connection
Equipment | [GROUNDED TRANSFORMER] | RatedVoltage | Volt | Rated voltage of the transformer | nominal_voltage |  | Volt | The nominal voltage of the winding.
Network | [THREE WINDING AUTO TRANSFORMER SETTING] | PrimaryBaseVoltage | kV | Base voltage primary
|  | SecondaryBaseVoltage |  | Base voltage secondary
|  | TertiaryBaseVoltage |  | Base voltage tertiary
| [THREE WINDING TRANSFORMER SETTING] | PrimaryBaseVoltage |  | Base voltage primary
|  | SecondaryBaseVoltage |  | Base voltage secondary
|  | TertiaryBaseVoltage |  | Base voltage tertiary
Equipment | [PHASE SHIFTER TRANSFORMER] | RatedVoltage | ? | ?
| [TRANSFORMER] | KVLLprim, KVLLsec | KV | Line to Line
[5 empty] | voltage_limit |  | Volt | The maximum voltage allowed on the PT secondary
[5 empty] | resistance |  | Per unit Ohm | The per unit resistance of the winding. For a representation with only one resistance for the entire transformer, this is split equally between the windings.
[5 empty] | reverse_resistance |  | Per unit Ohm | The per unit resistance of the winding with reverse powerflow. For a representation with only one resistance for the entire transformer, this is split equally between the windings.
[5 empty] | phase_windings |  | List(PhaseWinding) | A list of phasewinding objects which contain the phase, tap position and compensator settings
Equipment | [AUTOTRANSFORMER] | KVA | kVA | Total nominal rating according to type values. | rated_power |  | Volt-amperes | The rated power of the winding
| [THREE WINDING AUTO TRANSFORMER] | PrimaryRatedCapacity |  | Rated power for the primary
|  | SecondaryRatedCapacity |  | Rated power for the secondary
|  | TertiaryRatedCapacity |  | Rated power for the tertiary
| [THREE WINDING TRANSFORMER] | PrimaryRatedCapacity |  | Rated power for the primary
|  | SecondaryRatedCapacity |  | Rated power for the secondary
|  | TertiaryRatedCapacity |  | Rated power for the tertiary
| [TRANSFORMER] | KVA |  | Total nominal rating according to type values.
[5 empty] | emergency_power | None | Volt-Ampre | The emergency rating of the winding

## PhaseWinding
|  | CYME |  |  | DITTO
File | Header | Attribute | Units | Description | Attribute | Duplication Warning | Units | Description | Default
Network | [AUTO TRANSFORMER SETTING] | Tap | Float | Tap position | tap_position |  | Int | It should be in the range [-lowstep, highstep] provided by the transformer/regulator
| [THREE WINDING AUTO TRANSFORMER SETTING] | PrimaryFixedTapSetting
SecondaryFixedTapSetting
TertiaryFixedTapSetting
| [THREE WINDING TRANSFORMER SETTING] | PrimaryFixedTapSetting
SecondaryFixedTapSetting
TertiaryFixedTapSetting
Network | [AUTO TRANSFORMER SETTING] | PhaseON | Phase | Phase | phase |  | String | The phase for this componant of the winding
| [GROUNDINGTRANSFORMER SETTINGS] | Phase
[5 empty] | compensator_r |  | Volt | The compensator resistive value for the phase
[5 empty] | compensator_x |  | Volt | The compensator reactive value for the phase

## Regulator
| CYME |  |  |  | DITTO
File | Header | Attribute | Units | Description | Attribute | Duplication Warning | Units | Description | Default
Equipment | [REGULATOR] | ID | String | ID label of the regulator | name | None | String | The name of the Regulator object
[5 empty] | delay | None | seconds | The delay for the first tap change operation
[5 empty] | highstep | None | Int | The highest possible tap setting from neutral
[5 empty] | lowstep | None | Int | The lowest possible tap setting from neutral
Equipment | [REGULATOR] | PT | Float | PT Ratio (Vprimary/Vsecondary) | pt_ratio | None | Float | The turns ratio used for the power transducer with a line-drop compensator
Network | [REGULATOR SETTING]
[5 empty] | ct_ratio | None | Float | The turns ratio used for the current transducer with a line-drop compensator
[5 empty] | phase_shift | None | Degrees | The degree phase shift that the transformer causes
[5 empty] | ltc | None | Int | 1 if this regulator is a load tap changer, 0 otherwise
Equipment | [REGULATOR] | ForwardBandwidth | Volt | Forward Bandwidth | bandwidth | None | Volt | The band before a change occurs in the regulator
Network | [REGULATOR SETTING] | BandWidthA, BandWidthB… | Volt | Bandwdth setting of the regulator per phase
Network | [REGULATOR SETTING] | VsetA, VsetB, VsetC | Volt | Setting of the regulator per phase. | bandcenter | None | Volt | The target value for the regulator. Should often be the nominal voltage of the windings.
[5 empty] | voltage_limit | None | Volt | The maximum voltage allowed on the PT secondary
Network | [SECTION] | FromNodeID | String |  | from_element | None | String | Name of the node which connects to the 'from' end of the regulator
Network | [SECTION] | ToNodeID | String |  | to_element | None | String | Name of the node which connects to the 'to' end of the regulator
[5 empty] | reactances | None | List((Int,Int,Int)) | Reactances are described between all the windings. There are n*(n-1)/2 reactances (where n is the number of windings). For two a winding transformer this gives one value, and for a 3 winding transformer it gives 3. The list elements have (from_winding, to_winding, reactance) where from_winding and to_winding are the 1-based indices of the windings list.
[5 empty] | connected_transformer | None | String | The name of the transformer that the regulator is connected to
Network | [REGULATOR SETTING] | PhaseON | Phase | Phase | pt_phase | None | String | The phase number that's used to monitor the voltage
[5 empty] | windings | None | List(Winding) | This is a list containing one element for each winding in the voltage regulator. It describes attributes of the winding. This paramter is required to describe many compontants of the regulator. The simplest versions have two windings representing a high and low voltage.
[5 empty] | winding | None | Int | Number of the winding of the transformer element that the RegControl is monitoring
Equipment | [REGULATOR] | CT | Amps | CT primary rating | ct_prim | None | Float | Rating in Ampere of the primary CT rating for converting the line amps to control amps
Network | [REGULATOR SETTING]
[5 empty] | noload_loss | None | Float | The no-load loss for a zero sequence short-circuit test on the regulator
Network | [REGULATOR SETTING] | CoordX,CoordY | Float | X and Y coordinates of the regulator | positions |  |  | list of positional points describing the regulator

## PowerSource
| CYME |  |  |  | DITTO
File | Header | Attribute | Units | Description | Attribute | Duplication Warning | Units | Description | Default
Network | [SOURCE] | SourceID | String | ID of the source | name | None | String | Name of the power source object
Network | [SOURCE] | DesiredVoltage | kv |  | nominal_voltage | None | volts | This parameter defines the base voltage at the power source.
Network | [SECTION] | Phase | String | Get the section between source and feeder | phases | None | String | This parameter is a list of all the phases at the power source.
Network | [SECTION] | CoordX,CoordY |  |  | positions | None | List(Position) | This parameter is a list of positional points describing the power source - it should only contain one. The positions are objects containing elements of long, lat and elevation.
|  |  |  | Set to one if sourcebus | is_sourcebus | None | Integer | A Boolean flag which is 1 if the PowerSource object is an external power source at the distribution system head
Equipment | [SUBSTATION] | MVA | mva |  | rated_power | None | volt ampere | The rated power of the source node
[5 empty] | emergency_power | None | volt ampere | The emergency power of the source node
Equipment | [SUBSTATION] | Conn | String |  | connection_type | None | String | The connection type (D, Y, Z, A) for Delta, Wye, Zigzag or autotransformer.
[5 empty] | cutout_percent | None | float | The cutout percentage. If the per-unit power drops below this value the power source turns off
[5 empty] | cutin_percent | None | float | The cutin percentage. If the per-unit power rises above this value the power source turns on
[5 empty] | resistance | None | float | The per-unit internal resistance of the power source
[5 empty] | reactance | None | float | The per-unit internal reactance of the power source
[5 empty] | v_max_pu | None | float | The per-unit maximum voltage. Beyond this constant impedance model is applied
[5 empty] | v_min_pu | None | float | The per-unit minimum voltage. Below this, constant impedance model is applied
[5 empty] | power_factor | None | float | The power factor for the power source object
Network | [SECTION] | tonodeID | String |  | connecting_element | None | String | Name of the bus to which the power source is connected. This can be interpreted as "from" at a feeder head and "to" for a PV inverter