## Line
| GridLABD |  |  | DITTO
Object | Attribute | Units | Description | Attribute | Duplication Warning | Units | Description | Default
overhead_line/underground_line/fuse/switch | name | String | Name of the line | name | None |  | The name of the line object
|  |  |  | nominal_voltage |  | Volts | This parameter defines the base voltage of the wire. | None
overhead_line/underground_line | overhead_line/underground_line | String | Implicit from whether overhead_line or underground_line | line_type | None | String | Whether the line is overhead or underground | overhead
overhead_line/underground_line | length | feet | The length of the line | length | None | Meters | This parameter is the length of the Line | None
overhead_line/underground_line/fuse/switch | from | String | The name of the element that this line connects from | from_element | None | String | Name of the node which connects to the 'from' end of the line | None
overhead_line/underground_line/fuse/switch | to | String | The name of the element that this line connects to | to_element | None | String | Name of the node which connects to the 'to' end of the line | None
fuse |  |  | Implicit from the fact that the object is a fuse | is_fuse | Needs to be consistant with wire values. True if one or more of the wires is a fuse | Bool | This flag indicates whether or not the line is also a fuse | None
switch |  |  | Implicit from the fact that the object is a switch | is_switch | Needs to be consistant with wire values. True if one or more of wires is a switch | Bool | This flag indicates whether or not the line is also a switch | None
switch | operating_mode | String | BANKED if banked and INDIVIDUAL otherwise | is_banked | Needs to be consistent with all the switch positions of each phase. | Bool | This flag indicates whether or not the switch is banked. If this is true, the switch objects are controlled together | None
|  |  |  | faultrate | None | Float | The number of faults that occur per year | None
line_configuration | conductor_<A,B,C> | N/A | The lines and their phases (as well as extra properties) are obtained form the line_configuration and line_spacing objects. Not provided if a matrix representation is provided with no wires. | wires | None | List(Wire) | This parameter is a list of all the wires included on the line. The wires are objects containing elements of phase, X and Y. | None
|  |  |  | positions | None | List(Position) | This parameter is a list of positional points describing the line. The positions are objects containing elements of long, lat and elevation. The points can be used to map the position of the line. | None
line_configuration | z<1,2,3><1,2,3>-z<1,2,3><1,2,3> | Complex | The matrix representation for the impedance of the lines. | impedance_matrix | Needs to be consistent with wire values. It is either provided or derived from the wires. | List(List(Complex)) Ohms/meter | This provides the matrix representation of the line impedance in complex form. Computed from the values of GMR and distances of individual wires. Kron reduction is applied to make this a 3x3 matrix.
|  |  |  | capacitance_matrix | Needs to be consistent with wire values | List(List(Complex)) MicroSiemens/meter | This provides the matrix representation of the line capacitance in complex form. Computed from the values of diameter and distances of individual wires. Kron reduction is applied to make this t a 3x3 matrix.
|  |  |  | KEY | Not in gridlab-d

## Wire
| GridLABD |  |  | DITTO
Object | Attribute | Units | Description | Attribute | Duplication Warning | Units | Description | Default
line_configuration | conductor_<A,B,C,N> | String | The phase of the conductor is specified by what type of conductor is being used | phase | None | String | The phase (A, B, C, N, s1, s2) of the wire
|  |  |  | nameclass | None | String | The nameclass (e.g. 1/0_ACSR) of the wire
line_spacing | distance_<A,B,C,N,E><A,B,C,N,E> | feet | The distance between the different line phases. Several geometries are considered and the feasible one selected. | X | None | Meters | The horizontal placement of the wire on a cross section of the line w.r.t. some point of reference (typically one wire on the configuration)
line_spacing | distance_<A,B,C,N,E><A,B,C,N,E> | feet | TODO: Explain exact mapping of distances to geometries used in the code | Y | None | Meters | The vertical placement above (or below) ground of the wire on a cross section of the line w.r.t. some point of reference (typically one wire on the configuration)
overhead_line_conductor/underground_line_conductor | diameter/conductor_diameter | inches | The diameter of the conductor | diameter | None | Meters | The diameter of the conductor
overhead_line_conductor/underground_line_conductor | geometric_mean_radius/conductor_gmr | feet | The GMR of the wire | gmr | None | meters | The geometric mean radius of the wire
overhead_line_conductor/underground_line_conductor | rating.summer.continuous | Amps | The summer rating of the wire | ampacity | None | Amps | The ampacity rating of the wire under normal conditions
overhead_line_conductor/underground_line_conductor | rating.summer.emergency | Amps | The summer emergency rating of the wire | ampacity_emergency | None | Amps | The ampacity rating of the wire under emergency conditions
overhead_line_conductor/underground_line_conductor | resistance/conductor_resistance | Ohm/mile | The resistance per unit length of the wire | resistance | None | Ohms | The total resistance of the wire
fuse | phase_<A,B,C>_state | String | The existance of this attribute indicates that there is a fuse on this phase | is_fuse | None | Boolean | This flag indicates whether or not this wire is also a fuse
switch | phase_<A,B,C>_state | String | The existance of this attribute indicates that there is a switch on this phase | is_switch | None | Boolean | This flag indicates whether or not this wire is also a switch
fuse/switch | phase_<A,B,C>_state | String | GOOD/BLOWN for fuse and OPEN/CLOSED for a switch. | is_open | None | Boolean | This flag indicates whether or not this wire is open (if it is a switch/fuse)
fuse | current_limit | Amps | Assumed to be the same for all phases. | fuse_limit | None | Amps | This is the limit of the wire before the fuse blows
underground_line_conductor | neutral_gmr | feet | The GMR of the neutral wire | concentric_neutral_gmr | None | Meters | The geometric mean radius of the neutral for a concentric wire
underground_line_conductor | neutral_resistance | Ohm/mile | The resistance of the neutral wire per unit length | concentric_neutral_resistance | None | Ohms | The total resistance of the neutral for a concentric wire.
underground_line_conductor | neutral_diameter | inches | The diameter of the neutral wire | concentric_neutral_diameter | None | Ohms | The diameter of the neutral for a concentric wire.

## Node
| GridLABD |  |  | DITTO
Object | Attribute | Units | Description | Attribute | Duplication Warning | Units | Description | Default
Node | name | String | Name of the node | name | None |  | The name of the node object
Node | nominal_voltage | Volts | Node nominal voltage | nominal_voltage | None | Volts | The nomial voltage of this node
Node | phases | String | A string containing a list of all the phases at that node | phases | None | List(String) | A list of the different phases at this node
|  |  |  | positions | None | List(Position) | This parameter is a list of positional points describing the node - it should only contain one. The positions are objects containing elements of long, lat and elevation. | None

## Load
| GridLABD |  |  | DITTO
Object | Attribute | Units | Description | Attribute | Duplication Warning | Units | Description | Default
Load | name | String | Name of the load | name | None |  | The name of the load object
Load | nominal_voltage | Volts | Node nominal voltage | nominal_voltage | None | Volts | The nomial voltage of this node
|  |  |  | connection_type | None | String | The connection type (D, Y, Z, A) for Delta, Wye, Zigzag or autotransformer
|  |  |  | vmin | None | Float | The minimum per-unit voltage value. Going below this implies constant impedance
|  |  |  | vmax | None | Float | The maximum per-unit voltage value. Going below this implies constant impedance
|  |  |  | phase_loads | This has been adjusted from the original model so that all the load information is contained with different phases. | List(PhaseLoad) | This is a list of the different phase loads connected to the one load point. This contains information about the phase as well as the p&q or zip load data
|  |  |  | positions | None | List(Position) | This parameter is a list of positional points describing the load- it should only contain one. The positions are objects containing elements of long, lat and elevation. | None
|  |  |  | rooftop_area | None | m^2 | This parameter is the rooftop area for all phases of the load
|  |  |  | peak_p | Should be greater than the combined p values across all phaseloads | Watts | This paramter is the annual peak p value of all combined phases of the load
|  |  |  | peak_q | Should be greater than the combined q values across all phaseloads | Var | This paramter is the annual peak q value of all combined phases of the load
|  |  |  | peak_coincident_p | Should be greater than the combined p values across all phaseloads | Watts | This paramter is the annual coincident peak p value of all combined phases of the load
|  |  |  | peak_coincident_q | Should be greater than the combined q values across all phaseloads | Var | This paramter is the annual coincident peak q value of all combined phases of the load
|  |  |  | yearly_energy | Should be bound by the peak energy | WattHours | This is the total energy used by the load across all phases over a typical year

## PhaseLoad
| GridLABD |  |  | DITTO
Object | Attribute | Units | Description | Attribute | Duplication Warning | Units | Description | Default
Load or ZIPload | phases | String | Although phases lists all the phases, phase is deduced from whether attributes such as constant_power_A are provided. | phase | None | String | The phase (A, B, C, N, s1, s2) of the load
Load or ZIPload | constant_power_<A,B,C,S> | Volt-Ampres | The complex power for the load. The correct phase must be selected. P is defined by the real componant | p | This is done specifically for this phase and is used when use_zip is 0 | Watts | The active power of the load which is fixed. Positive values represent flow out of the node.
Load or ZIPload | base_power_<A,B,C,S>, pf_<A,B,C,S> | Volt-Ampres | The complex power for the load. This is used for ZIP loads. The real part is computed by using the power factor for Z I and P, weighted by the fraction they are used
Load or ZIPload | constant_power_<A,B,C,S> | Volt-Ampres | The complex power for the load. The correct phase must be selected. Q is defined by the imaginary componant | q | This is done specifically for this phase and is used when use_zip is 0 | Var | The reactive power of the load which is fixed. Positive values represent flow out of the node.
Load or ZIPload | base_power_<A,B,C,S>, pf_<A,B,C,S> | Volt-Ampres | The complex power for the load. This is used for ZIP loads. The imaginary part is computed by using the power factor for Z I and P, weighted by the fraction they are used
Load or ZIPload |  |  | Determined from whether the gridlab-d file contains information on the fraction of power used. | use_zip | None | Int | Describes whether the load is reprsented as a zipload or not. 1 represents zipload with fractions taken from the p and q values above. 0 represents a load defined by p & q alone.
Load or ZIPload | current_fraction_<A,B,C,S> current_pf_<A,B,C,S> | Float, Float | The fraction of current and the power factor from the base_power. Used to compute the real zip current | ppercentcurrent | This is the portion of active power load modelled by constant current. Active portions of current, power and impedance should all add to 1. Used for ZIP models.
Load or ZIPload | current_fraction_<A,B,C,S> current_pf_<A,B,C,S> | Float, Float | The fraction of current and the power factor from the base_power. Used to compute the imaginary zip current | qpercentcurrent | This is the portion of reactive power load modelled by constant current. Reactive portions of current, power and impedance should all add to 1. Used for ZIP models.
Load or ZIPload | power_fraction_<A,B,C,S> power_pf_<A,B,C,S> | Float, Float | The fraction of power and the power factor from the base_power. Used to compute the real zip power | ppercentpower | This is the portion of active power load modelled by constant power. Active portions of current, power and impedance should all add to 1. Used for ZIP models.
Load or ZIPload | power_fraction_<A,B,C,S> power_pf_<A,B,C,S> | Float, Float | The fraction of power and the power factor from the base_power. Used to compute the imaginary zip power | qpercentpower | This is the portion of reactive power load modelled by constant power. Reactive portions of current, power and impedance should all add to 1. Used for ZIP models.
Load or ZIPload | impedance_fraction_<A,B,C,S> impedance_pf_<A,B,C,S> | Float, Float | The fraction of impedance and the power factor from the base_power. Used to compute the real zip impedance | ppercentimpedance | This is the portion of active power load modelled by constant impedance. Active portions of current, power and impedance should all add to 1. Used for ZIP models.
Load or ZIPload | impedance_fraction_<A,B,C,S> impedance_pf_<A,B,C,S> | Float, Float | The fraction of impedance and the power factor from the base_power. Used to compute the imaginary zip impedance | qpercentimpedance | This is the portion of reactive power load modelled by constant impedance. Reactive portions of current, power and impedance should all add to 1. Used for ZIP models.

## Capacitor
| GridLABD |  |  | DITTO
Object | Attribute | Units | Description | Attribute | Duplication Warning | Units | Description | Default
Capacitor | name | String | Name of the capacitor | name | None |  | The name of the capacitor object
Capacitor | nominal_voltage | Volts | Node nominal voltage | nominal_voltage | None | Volts | The nomial voltage of the capacitor
|  |  |  | connection_type | None | String | This is the type of connection that the capacitor has. The connection type (D, Y, Z, A) for Delta, Wye, Zigzag or autotransformer
Capacitor | time_delay | seconds | Time delay before a switching operation takes place | delay | None | seconds | The time that the capacitor needs to connect or disconnect by automatic regulation
Capacitor | control | String | One of Var, Volt, VoltVar, Manual. | mode | None | String | What control mode is used. A string from one of the options: {voltage, activePower, reactivePower, currentFlow, admittance, timeScheduled, none}
Capacitor | voltage_set_low, VAr_set_low | Volts, Var | The low value being set for the controller | low | None | Volts, Var, Watt | The low value of range of the type being controllee by the capacitor (e.g. voltage)
Capacitor | voltage_set_high, VAr_set_high | Volts, Var | The high value being set for the controller | high | None | Volts, Var, Watt | The high value of range of the type being controllee by the capacitor (e.g. voltage)
|  |  |  | resistance | None | Ohms | The total series resistance of the capacitor
|  |  |  | resistance0 | None | Ohms | The total zero-sequence series resistance of the capacitor
|  |  |  | reactance | None | Ohms | The total series reactance of the capacitor
|  |  |  | reactance0 | None | Ohms | The total zero-sequence series reactance of the capacitor
|  |  |  | susceptance | This should match the formula of -1*VAR/(voltage)^2 where var is the total Var of the capacitor and voltage is the nominal voltage | Siemens | The total positive sequence shunt susceptance of the capacitor.
|  |  |  | susceptance0 | None | Siemens | The total zero sequence shunt susceptance of the capacitor.
|  |  |  | conductance | None | Siemens | The total shunt conductance of the capacitor
|  |  |  | conductance0 | None | Siemens | The total zero sequence shunt conductance of the capacitor
|  |  |  | pt_ratio | None | Float | The voltage (potential) transformer ratio used to step down the voltage for the controller
|  |  |  | ct_ratio | None | Float | The current transformer ratio used to define the current ratio for a controller.
Capacitor | pt_phase | String | The phase that the controller is connected to | pt_phase | None | String | The phase that the controller is connected to
Capacitor | parent | String | The name of the node that the cap connects to. This is done through a parent relationship. | connecting_element | None | String | The name of the node that the capacitor connects to
|  |  |  | positions | None | List(Position) | This parameter is a list of positional points describing the capacitor - it should only contain one. The positions are objects containing elements of long, lat and elevation. | None
|  |  |  | phase_capacitors | None | List(PhaseCapacitor) | A list of phase capacitors which contain phase, var and switch values. The total var of the capacitor is defined through the phasecapacitors

## PhaseCapacitor
| GridLABD |  |  | DITTO
Object | Attribute | Units | Description | Attribute | Duplication Warning | Units | Description | Default
Capacitor | phases | String | Although phases lists all the phases, phase is deduced from whether attributes such as capacitor_A are provided. | phase | None | String | The phase (A, B, C, N, s1, s2) of the capacitor section
| capacitor_<A,B,C> | Mvar | This is provided for each phase. Note that a unit is typically given after the value for this element | var | None | var | The var value of the capacitor phase
| switch_<A,B,C> | String | OPEN or CLOSED to denote whether the phase is connected in | switch | None | Int | A boolean value to denote whether or not the capacitor is switched in. 1 means it's switched in, 0 means that it's not.
|  |  |  | sections | None | Int | The maximum number of sections that can be connected to this phase
|  |  |  | normalsections | None | Int | The normal number of sections that are connected to this phase.

## Transformer
| GridLABD |  |  | DITTO
Object | Attribute | Units | Description | Attribute | Duplication Warning | Units | Description | Default
Transformer | name | String | Name of the transformer | name | None |  | The name of the transformer object
transformer_configuration | power_rating | kilo-Volt Ampres | This is the power rating of the entire transformer. All phases are assumed to have the same kVA rating | rated_power | This may be provided separately for each phase. Most applications just provide it for the whole transformer though. | Volt-Ampre | The rating of the entire transformer
|  |  |  | emergency_power | None | Volt-Ampre | The emergency rating of the entire transformer
transformer_configuration | install_type | String | Describes the install type for the transformer: {UNKNOWN, POLETOP, PADMOUNT, VAULT} | install_type | None | String | The mounting of the transformer: one of {POLEMOUNT, PADMOUNT, VAULT}
transformer_configuration | no_load_loss | per unit Ohm | The total no-load loss for the entire transformer. Note that the load loss is described by the resistances. | noload_loss | None | per unit Ohm | The no-load loss for a zero sequence short circuit test across the entire transformer.
|  |  |  | phase_shift | None | Degrees | The degree phase shift that the transformer causes
Transformer | from_node | String | The node that the transformer connects to on the high side of the transformer | from_element | None | String | Name of the node which connects to the 'from' end of the transformer
Transformer | to_node | String | The node that the transformer connects to on the low side of the transformer | to_element | None | String | Name of the node which connects to the 'to' end of the transformer
transformer_configuration | reactance/impedance, impedance1 impedance2 |  | For two winding transformers, the reactance is from either reactance or the imaginary part of impedance. For center tap the additional values of impedance1 and impedance2 are also provided. The imaginary parts are used to create the reactances. | reactances | None | List((Int,Int,Int)) | Reactances are described between all the windings. There are n*(n-1)/2 reactances (where n is the number of windings). For two a winding transformer this gives one value, and for a 3 winding transformer it gives 3. The list elements have (from_winding, to_winding, reactance) where from_winding and to_winding are the 1-based indices of the windings list.
|  |  |  | windings | None | List(Winding) | A list of the windings that the transformer contains. Most will have two windings but center tap transformers have three.
|  |  |  | positions | None | List(Position) | This parameter is a list of positional points describing the transformer - it should only contain one. The positions are objects containing elements of long, lat and elevation.

## Winding
| GridLABD |  |  | DITTO
Object | Attribute | Units | Description | Attribute | Duplication Warning | Units | Description | Default
Transformer_configuration | connect_type | String | This is one of {Wye-Wye, Delta-Delta, Delta-Gwye, Single phase, Single phase center tapped}. For single phase and centre tapped, no connection types are defined. | connection_type |  | String | The connection type (D, Y, Z, A) for Delta, Wye, Zigzag or autotransformer
|  |  | A high and low winding are created for non-center tap transformers, which have two low windings | voltage_type |  | Int | 0 for a high voltage connection, 2 for a low voltage connection and 1 for an intermediate connection
transformer_configuration | primary_voltage,secondary_voltage | Volt | The primary and secondary voltages for the transformer. These give the nominal voltage for each winding | nominal_voltage |  | Volt | The nominal voltage of the winding.
|  |  |  | voltage_limit |  | Volt | The maximum voltage allowed on the PT secondary
transformer_configuration/regulator_configuration |  |  |  | resistance |  | Per unit Ohm | The per unit resistance of the winding. For a representation with only one resistance for the entire transformer, this is split equally between the windings.
|  |  |  | reverse_resistance |  | Per unit Ohm | The per unit resistance of the winding with reverse powerflow. For a representation with only one resistance for the entire transformer, this is split equally between the windings.
|  |  |  | phase_windings |  | List(PhaseWinding) | A list of phasewinding objects which contain the phase, tap position and compensator settings

## PhaseWinding
| GridLABD |  |  | DITTO
Object | Attribute | Units | Description | Attribute | Duplication Warning | Units | Description | Default
regulator_configuration | tap_pos_<A,B,C> | Int | The initial tap position for each phase of the winding. It should be in the range [-lowstep, highstep] provided by the transformer/regulator | tap_position |  | Int | It should be in the range [-lowstep, highstep] provided by the transformer/regulator
transformer, regulator | phases | String | The phases associated with the transformer. If one of these is S then it is assigned to the low voltage winding. | phase |  | String | The phase for this componant of the winding
regulator_configuration | compensator_r_setting_<A,B,C> | Volt | The compensator resistive value for the phase | compensator_r |  | Volt | The compensator resistive value for the phase
regulator_configuration | compensator_x_setting_<A,B,C> | Volt | The compensator reactive value for the phase | compensator_x |  | Volt | The compensator reactive value for the phase

## Regulator
| GridLABD |  |  | DITTO
Object | Attribute | Units | Description | Attribute | Duplication Warning | Units | Description | Default
Regulator | name | String | Name of the transformer | name | None | String | The name of the Regulator object
Regulator_configuration | time_delay | seconds | The time between the change request and the physical changing of the regulator | delay | None | seconds | The delay for the first tap change operation
Regulator_configuration | raise_taps | Int | Upper limit of tap positions allowed in the regulator | highstep | None | Int | The highest possible tap setting from neutral
Regulator_configuration | lower_taps | Int | Lower limit of tap positions allowed in the regulator | lowstep | None | Int | The lowest possible tap setting from neutral
Regulator_configuration | power_transducer_ratio | Float | The turns ratio for the power transducer | pt_ratio | None | Float | The turns ratio used for the power transducer with a line-drop compensator
Regulator_configuration | current_transducer_ratio | Float | The turns ratio for the current transducer | ct_ratio | None | Float | The turns ratio used for the current transducer with a line-drop compensator
|  |  |  | phase_shift | None | Degrees | The degree phase shift that the transformer causes
|  |  |  | ltc | None | Int | 1 if this regulator is a load tap changer, 0 otherwise
Regulator_configuration | bandwidth | Volt | Allowable symmetrical range before a change is implemented. | bandwidth | None | Volt | The band before a change occurs in the regulator
Regulator_configuration | band_center | Volt | The centerpoint for the desired voltage target | bandcenter | None | Volt | The target value for the regulator. Should often be the nominal voltage of the windings.
Regulator | from_node | String | The node that the transformer connects to on the high side of the transformer | from_element | None | String | Name of the node which connects to the 'from' end of the regulator
Regulator | to_node | String | The node that the transformer connects to on the low side of the transformer | to_element | None | String | Name of the node which connects to the 'to' end of the regulator
|  |  |  | reactances | None | List((Int,Int,Int)) | Reactances are described between all the windings. There are n*(n-1)/2 reactances (where n is the number of windings). For two a winding transformer this gives one value, and for a 3 winding transformer it gives 3. The list elements have (from_winding, to_winding, reactance) where from_winding and to_winding are the 1-based indices of the windings list.
|  |  |  | connected_transformer | None | String | The name of the transformer that the regulator is connected to
Regulator_configuration | pt_phase | String | Phase that the power transducer is connected to | pt_phase | None | String | The phase number that's used to monitor the voltage